## Sheet1
Device | Number | Location | Accuracy Measurement | Recommendations | Comments from SINTEF, updated 15 nov 2022:
Flat/appartment (Requiers consent from residents)
T/H/CO2 |  |  | .+-0.3; +-5%, +-100ppm | h. = 1.5m, Away from heat sources and windows | Temperature logging data available in BMS. There is no Humidity or CO2 sensors in flat. CO2 sensors can possibly be mounted in ventilation duct. Data access requires consent from residents.
Luminosity and occupancy |  |  |  | in the middle of the room | No sensors installed.
Contact Sensor (window) |  |  | 0/1 |  | Not installed, but can be installed at extra cost. Also requires consent from residents.
Luminosity and Occupancy |  |  | .+-50lux |  | Not installed lightsensor, occupance sensor.
Electricity overall flat |  |  |  |  | Data not available in BMS. Data availabe at powergrid operator, but access requires consent. Data need to be exportet manually. We are working on consent. We can transfer data at aggregated level with resolution of 6 appartments (one floor or one facade)
Electricity light |  |  |  |  | No meter installed, but value can possibly be calculated.
Thermostat signal |  |  |  |  | On off signal. Available in BMS.
Electricity of Mecanical Ventilation |  |  |  |  | Power usage is part of overall electrical consumption per appartment (se above). Values on fan power and electric heater relative load is however available in BMS (read only data).
COMMON AREAS
Common areas
T/H/CO2 |  |  | .+-0.3; +-5%, +-100ppm | h. = 1.5m, Away from heat sources and windows | Temperature and CO2 (for areas with DCV) logging ok. data in BMS already. No Humidity sensors
Luminosity and occupancy |  |  |  | in the middle of the room | Occupancy sensor installed in some common areas, but it is not connected to BMS (no data available). 1. Corridor, wardoffice-automatic by occupance sensor. 2.Common livingroom, kitchen, gymnasium-semiautomatic: must be turned on manually- kept on by occupance sensor. 3. Outside light: Astro-clock 4. No luminosity sensors installed
Contact Sensor (window) |  |  | 0/1 |  | not installed.
Electricity overall |  |  |  |  | Data is available in BMS and logfiles can be made and sent.
Electricity light |  |  |  |  | Can be calculated? Not available
Thermostat signal |  |  |  |  | on/off- Data available.
Electricity of Mecanical Ventilation |  |  |  |  | Combined meter for technical equipment excl HP and Boiler (Fans, pumps, control etc). Data is availabel in BMS. Logfiles can be made and sent
OVERALL BUILDING (ACUMMULATED)
Weather station (Solar radiation, Temperature, Humidity, Sensor Rain) |  |  | Solar radation: accuracy +-5%. Temperature: +- 0.3C, Humidity; +-5% | Far away from heat source and shading elements | Weather station not installed. Solar sensor communnicates with window blinds. Not incorporateed in BMS. No control or datalogging availabel. Outdoor temperatrue sensor is installed and logged.
Electricity consumption |  |  |  |  | Data is availabel in BMS. Logfiles can be made and sent. For common areas only. See point on appartments above
Electricity consumption of HP |  |  |  |  | Data is availabel in BMS. Logfiles can be made and sent
Thermal porduction of HP |  |  |  |  | Data is availabel in BMS. Logfiles can be made and sent
Electricity Production from PV system |  |  |  |  | To be installed in HMS soon Net electricity production for PV is expected to be available in BMS soon
Electricity consumption of PV system |  |  |  |  | To be installed in HMS soon. Not available
Elctricity consumption used by PV system |  |  |  |  | To be installed in HMS soon. What is the difference from the one above?